## Inputs
Inputs
deltaflowC2 Selector 3.07
Project Details
Customer line 1
Customer line 2
Customer line 3
Serial Number
Tag Number
Comments
|  |  |  | Primärelement | 0
Primary Element | [5 empty] | Nr | ID | id | Beta | C | KEPS | dpLoss Faktor | Comment | 0
Meter Type DFC2- | P10 |  |  |  | P10 | 1 | 10000 | 25 |  |  |  | 0.20941 | P10 insertion probe type for pipes >25mm | 0
P10 insertion probe type for pipes >25mm |  |  |  |  | V40(20mm) | 2 | 35 | 20 | 0.57143 | 0.942 | 780 | 0.4554 | R 1 1/2" male venturi type ID 35x20x35mm | 0
Pipe Inside Diameter | 50 | [mm] |  |  | V25(15mm) | 3 | 25 | 15 | 0.6 | 0.981 | 765 | 0.528 | R 1" male venturi type ID 25x15x25mm | 0
Neck Diameter | 22.5 | [mm] |  |  | V20(10mm) | 4 | 15 | 10 | 0.66667 | 0.948 | 740 | 0.561 | R 3/4" male venturi type ID 15x10x15mm | 0
Probe Resistance Zeta z | 2.8375 | [-] |  |  | V20(8mm) | 5 | 15 | 8 | 0.53333 | 0.939 | 631 | 0.711 | R 3/4" male venturi type ID 15x8x15mm | 0
Flow Coefficient C | 0.97398 | [-] |  |  | V20(6mm) | 6 | 15 | 6 | 0.4 | 0.9285 | 570 | 0.827 | R 3/4" male venturi type ID 15x6x15mm | 0
[5 empty] | V20(4mm) | 7 | 15 | 4 | 0.26667 | 0.9012 | 581 | 0.877 | R 3/4" male venturi type ID 15x4x15mm | 0
ImprooveIT Factor | 1 | [-] |  |  | pitot tube | 8 | 10000 | 1 |  |  |  | 0 | other pitot tube, design from manufacturer needed | 0
[5 empty] | venturi/orifice | 9 | 10000 | 1 | 0.45 | 0.97398 |  | 0 | other venturi/orifice, design from manufacturer needed | 0
|  |  |  | Aktuelle Auswahl | P10 | 1 | 10000 | 25 | 0 | 0 | 0 | 0.20941
Medium | other gas | - |  | Typ |  | 1
Norm Density | 12321 | [kg/Nm³] | 0°C, 1013,25 hPa
Process Data
Design Pressure | 100 | [kPa]
Design Temperature | 19 | [°C] |  | Medium | 0
Design Flow | 450 | [Nm3/h]@0°C/1013,25mbar | Too high |  |  |  | Formel | Molare Masse | Schmelzpunkt | Siedepunkt | Kritische Temperatur | Protoscher drtuck | Azentrischer Faktor | Normdichte | Visk Parameter A | Visk Parameter B | Isentropencoeffizient | 0
Design Expansionnumber | 0.957 | [-] | [5 empty] | g/mol | °C | °C | °C | bar | [-] | kg/Nm³ | 0
Design Differential Pressure | 71.052 | [mbar] |  |  | Air | 1 | - | 28.96 | -200 | -194,35 | -141.65 | 36.6 |  | 1.2929 | 150.3 | 123.6 | 1.4015
[5 empty] | other gas | 2 | -
[5 empty] | Ammoniak | 3 | NH3 | 17.031 | -77.72 | -33.35 | 132.3 | 113 | 0.25 | 0.769 | 159.0062 | 513 | 1.3031
Results |  |  |  |  | Argon | 4 | Ar | 39.948 | -189.3 | -185.87 | -122.43 | 48.74 | 0.0001 | 1.7838 | 231.48 | 228.26 | 1.6855
dp Design | 71.052 | [mbar] |  |  | iso-Butane | 5 | C4H10 | 58.12 | -159.4 | -11.73 | 134.98 | 37.2 | 0.183 | 2.697 | 85.79 | 299.02 | 1.0714
Expansion Number | 0.957 | [-] |  |  | Helium | 6 | He | 4.0026 | -271.15 | -268.934 | -267.95 | 2.275 | -0.365 | 0.1785 | 136 | 55 | 1.6674
pressure Loss | 20.94% |  |  |  | Carbon Dioxide | 7 | CO2 | 44.01 | -56.56 | -78.5 | 31 | 73.8 | 0.239 | 1.9769 | 165.5 | 274 | 1.2898
DesignFlow is too high or wrong p&T! Please select other Type or Diameter |  |  |  |  | Carbon Monoxide | 8 | CO | 28.01 | -205.1 | -191.5 | -140.2 | 35 | 0.066 | 1.2505 | 86.72 | 131.74 | 1.4008
[5 empty] | Methane | 9 | CH4 | 16.0426 | -182.48 | -161.49 | -82.1 | 46.4 | 0.011 | 0.718 | 88.953 | 125 | 1.306
Meter options |  |  |  |  | Neon | 10 | Ne | 20.1796 | -248.61 | -246 | -228.7 | 27.3 |  | 0.8999 | 201 | 35 | 1.6677
I/O Variant | Outputs 4..20mA and 0..10VDC (4 pin M12 Plug) | IO |  |  | Propane | 11 | C3H8 | 44.096 | -187.69 | -42.04 | 96.8 | 42.5 | 0.153 | 2.011 | 107 | 376 | 1.1193
Display | integrated display / keypad | D1 |  |  | Oxygene | 12 | O2 | 31.9988 | -218.65 | -182.96 | -118.57 | 50.4 |  | 1.429 | 174.7 | 138 | 1.3692
Accuracy | High Precision 1% o.S. 1:10 incl 5 point calibration | DH |  |  | Nitrogene | 13 | N2 | 28.013 | -209.8 | -195.81 | -146.85 | 34 | 0.039 | 1.2503 | 137.8 | 103 | 1.421
Accessories | none | - |  |  | Hydrogene | 14 | H2 |  |  |  | -239.96 | 13.15 | -0.216 | 0.0899 | 73.57 | 122 | 1.4069
Typecode | P10-IO-D1-DH-- |  |  | Aktuelle Auswahl | other gas | 2 | - | 0 | 0 | 0 | 0 | 0 | 0 | 12321 | 0 | 0 | 0
|  |  |  | Berechnungen | Dichte bei Designpunkt |  |  | 11369.0626 | kg/m³
Meter Settings |  |  |  |  | Dichte bei Auslgungspunkt |  |  | 194558.1051 | kg/m³
Flow Unit / Time Basis | [Nm3/h]@0°C/1013,25mbar
Flowspan | 26.8158 |  |  | Druck | [6 empty] | Differenzdruck | 0
Temp. Unit | [°C] | [5 empty] | Faktor zu Pa | [6 empty] | Faktor zu Pa | 0
Press. Unit | [kPa] |  |  |  | [mbar abs] | 1 | 100 |  |  |  |  | [mbar] | 1 | 100
T. type | Pitot |  |  |  | [bar abs] | 2 | 100000 |  |  |  |  | [bar] | 2 | 100000
dp press. Unit | [mbar] |  |  |  | [kPa] | 3 | 1000 |  |  |  |  | [kPa] | 3 | 1000
Damping | select [0..99] sek |  |  |  | [hPa] | 4 | 100 |  |  |  |  | [hPa] | 4 | 100
Current Out | select [Flow/dp/p/T] |  |  |  | [PSI] | 5 | 6894.76 |  |  |  |  | [PSI] | 5 | 6894.76
Voltage Out | select [Flow/dp/p/T] |  |  |  | [Torr] | 6 | 133.322 |  |  |  |  | [Torr] | 6 | 133.322
Modbus Brate | select [4800..38400] |  |  | Aktuelle Auswahl | [kPa] | 3 | 1000 |  |  |  | Aktuelle Auswahl | [mbar] | 1 | 100
Pulse Length | select[2, 10, 100] mS |  |  | Berechnungen | Designdruck in Pa |  | 100000 | Pa |  |  | Berechnungen | Designdp in Pa |  | 7105.2 | Pa | 0
Pulse Count | select [0..9] p/unit
0-Suppression | select [0..20%] of Flowspan
KEPS | 2001.4916 |  |  | Temperatur | 0
K Analog | 314042.8655 |  |  |  | [°C] | 1 | 0 | 1
[5 empty] | [K] | 2 | -273.15 | 1
[5 empty] | [°F] | 3 | -32 | 0.55556
|  |  |  | Aktuelle Auswahl | [°C] | 1 | 0 | 1
|  |  |  | Berechnungen | Designtemperatur in °C |  | 19 | °C
[5 empty] | Designtemperatur in K |  | 292.15 | K
|  |  |  | Durchfluss |  | Nr | ConvFactor | Vol(2) or Mass (1) | 0
[5 empty] | [kg/s] | 1 | 1 | 1
[5 empty] | [kg/min] | 2 | 0.016667 | 1
[5 empty] | [kg/h] | 3 | 0.00027778 | 1
[5 empty] | [t/s] | 4 | 1000 | 1
[5 empty] | [t/min] | 5 | 16.6667 | 1
[5 empty] | [t/h] | 6 | 0.27778 | 1
[5 empty] | [g/s] | 7 | 0.001 | 1
[5 empty] | [g/min] | 8 | 1.6667e-05 | 1
[5 empty] | [g/h] | 9 | 2.7778e-07 | 1
[5 empty] | [Nm3/s]@0°C/1013,25mbar | 10 | 1 | 1
[5 empty] | [Nm3/min]@0°C/1013,25mbar | 11 | 0.016667 | 1
[5 empty] | [Nm3/h]@0°C/1013,25mbar | 12 | 0.00027778 | 1
[5 empty] | [Nl/s]@0°C/1013,25mbar | 13 | 0.001 | 1
[5 empty] | [Nl/min]@0°C/1013,25mbar | 14 | 1.6667e-05 | 1
[5 empty] | [Nl/h]@0°C/1013,25mbar | 15 | 2.7778e-07 | 1
[5 empty] | [cft/s]@process p&T | 16 | 0.028317 | 2
[5 empty] | [cft/min]@process p&T | 17 | 0.00047195 | 2
[5 empty] | [cft/h]@process p&T | 18 | 7.8658e-06 | 2
[5 empty] | [l/s]@process p&T | 19 | 0.001 | 2
[5 empty] | [l/min]@process p&T | 20 | 1.6667e-05 | 2
[5 empty] | [l/h]@process p&T | 21 | 2.7778e-07 | 2
[5 empty] | [m3/s]@process p&T | 22 | 1 | 2
[5 empty] | [m3/min]@process p&T | 23 | 0.016667 | 2
[5 empty] | [m3/h]@process p&T | 24 | 0.00027778 | 2
|  |  |  | Aktuelle Auswahl | [Nm3/h]@0°C/1013,25mbar | 12 | 0.00027778 | 1
|  |  |  | Berechnungen | Durchfluss | 1540.125 | [kg/s]
4
|  |  |  | Auslegungspunkt DFC2 Elektronik | Massflow (1) |  | VolFlow (2) |  | Massflow (1)
|  |  |  | dp | 20000 | Pa | 20000 | Pa | 20000
|  |  |  | pabs | 1600000 | Pa | 100000 | Pa | 1600000
|  |  |  | T | 273.15 | K | 273.15 | K | 273.15
|  |  |  | KEPS | 0 | [-] | 0 | [-] | 0
|  |  |  | FLOWMAX [Digitalwert] | 18714 | [-] | 11249 | [-] | 18714
|  |  |  | Berechnungen Sonden | [10 empty] | Epsilon Auslegung | dp design (Epsiolon 1) Pa | Epsilon Design | dploss
|  |  |  | P10 |  | Blockage | 0.33614 | Kwert | 0.52985 | Zeta | 3.5621 | KEPS | 2001.4916 | -1.4916 | 1 | 96382741.849 | 2.3711
|  |  |  | Andere Sonden |  |  |  | Kwert | 0.59365 | Zeta | 2.8375 | KEPS | 634.5883 |  | 0.99244 | 65072.9031 | 0.957
|  |  |  | Andere Venturi/Blende | [7 empty] | KEPS | 634.5883 |  | 0.99244 | 65072.9031 | 0.957
|  |  |  | V20-V40 | [7 empty] | KEPS | 0 |  | 1 | #DIV/0! | #DIV/0!
|  |  |  | Berechnung FlowSpan | (Epsilon =1, gem HA)
Usereinheit
|  |  |  | P10 | 91.777 | kg/s | 26.8158 | [Nm3/h]@0°C/1013,25mbar
|  |  |  | Andere Sonde | 102.8296 | kg/s | 30.0452 | [Nm3/h]@0°C/1013,25mbar
|  |  |  | Andere Venturi | 35.6241 | kg/s | 10.4088 | [Nm3/h]@0°C/1013,25mbar
|  |  |  | V20-V40 | 0 | kg/s | 0 | [Nm3/h]@0°C/1013,25mbar
|  |  |  | FlowSpan | 26.8158 | [Nm3/h]@0°C/1013,25mbar
|  |  |  | Berechnung K Analog | 3.7453 | K,Value
314042.8655
Berechnung KEPS
|  |  |  | P10 | 2001.4916
|  |  |  | Andere Sonde | 634.5883
|  |  |  | Andere Venturi | 634.5883
|  |  |  | V20-V40 | 0
|  |  |  | KEPS | 2001.4916
Berechnung dp Design
[5 empty] | dp[Pa] | dp[Usereinheit] |  | Expansionszahl
|  |  |  | P10 | 17143979.9804 | 171439.7998 | [mbar] | 2.3711
|  |  |  | Andere Sonden | 83831346.0621 | 838313.4606 | [mbar] | 0.957
|  |  |  | Andere Venturi/Blende | 728348573.7133 | 7283485.7371 | [mbar] | 0.957
|  |  |  | V20-V40 | #DIV/0! | #DIV/0! | [mbar] | #DIV/0!
|  |  |  | dp | 17143979.9804 | 171439.7998 | [mbar] | 2.3711
Berechnung Unsicherheit
|  |  |  | Flow [Nm3/h]@0°C/1013,25mbar | dp [Pa] | dp Fehler Nach Nullpunktabgleich | Fehler durch dp | Fehler durch Dichte und Primärelement mit Klaib | Unsicherheit abs mit Kalbirierung | Unicherheit r.M. mit Kalibrierung | dp Fehler ohne Kalibroierung | Fehler durch dp | Unsicherheit Abs ohne Kalibrierung | Unsicherheit d.M. ohne Kalibrierung
|  |  |  | 450 | 17143979.9804 | 85729.8999 | 0.2497% | 0.25% | 0.4997% | 0.4997% | 171469.7998 | 0.4988% | 2.499% | 2.499%
|  |  |  | 427.5 | 15472441.9323 | 77372.2097 | 0.2497% | 0.25% | 0.4997% | 0.4747% | 154754.4193 | 0.4989% | 2.499% | 2.374%
|  |  |  | 405 | 13886623.7841 | 69443.1189 | 0.2497% | 0.25% | 0.4997% | 0.4498% | 138896.2378 | 0.4989% | 2.499% | 2.249%
|  |  |  | 382.5 | 12386525.5358 | 61942.6277 | 0.2497% | 0.25% | 0.4997% | 0.4248% | 123895.2554 | 0.4989% | 2.499% | 2.124%
|  |  |  | 360 | 10972147.1874 | 54870.7359 | 0.2497% | 0.25% | 0.4997% | 0.3998% | 109751.4719 | 0.4989% | 2.499% | 1.999%
|  |  |  | 337.5 | 9643488.739 | 48227.4437 | 0.2497% | 0.25% | 0.4997% | 0.3748% | 96464.8874 | 0.4989% | 2.499% | 1.874%
|  |  |  | 315 | 8400550.1904 | 42012.751 | 0.2497% | 0.25% | 0.4997% | 0.3498% | 84035.5019 | 0.4989% | 2.499% | 1.749%
|  |  |  | 292.5 | 7243331.5417 | 36226.6577 | 0.2498% | 0.25% | 0.4998% | 0.3248% | 72463.3154 | 0.499% | 2.499% | 1.624%
|  |  |  | 270 | 6171832.7929 | 30869.164 | 0.2498% | 0.25% | 0.4998% | 0.2999% | 61748.3279 | 0.499% | 2.499% | 1.499%
|  |  |  | 247.5 | 5186053.9441 | 25940.2697 | 0.2498% | 0.25% | 0.4998% | 0.2749% | 51890.5394 | 0.499% | 2.499% | 1.374%
|  |  |  | 225 | 4285994.9951 | 21439.975 | 0.2498% | 0.25% | 0.4998% | 0.2499% | 42889.95 | 0.4991% | 2.499% | 1.25%
|  |  |  | 202.5 | 3471655.946 | 17368.2797 | 0.2498% | 0.25% | 0.4998% | 0.2249% | 34746.5595 | 0.4992% | 2.499% | 1.125%
|  |  |  | 180 | 2743036.7969 | 13725.184 | 0.2499% | 0.25% | 0.4999% | 0.1999% | 27460.368 | 0.4993% | 2.499% | 0.9997%
|  |  |  | 157.5 | 2100137.5476 | 10510.6877 | 0.2499% | 0.25% | 0.4999% | 0.175% | 21031.3755 | 0.4995% | 2.499% | 0.8748%
|  |  |  | 135 | 1542958.1982 | 7724.791 | 0.25% | 0.25% | 0.5% | 0.15% | 15459.582 | 0.4997% | 2.5% | 0.7499%
|  |  |  | 112.5 | 1071498.7488 | 5367.4937 | 0.2502% | 0.25% | 0.5002% | 0.125% | 10744.9875 | 0.5001% | 2.5% | 0.625%
|  |  |  | 90 | 685759.1992 | 3438.796 | 0.2504% | 0.25% | 0.5004% | 0.1001% | 6887.592 | 0.5009% | 2.501% | 0.5002%
|  |  |  | 67.5 | 385739.5496 | 1938.6977 | 0.251% | 0.25% | 0.501% | 0.07515% | 3887.3955 | 0.5026% | 2.503% | 0.3754%
|  |  |  | 45 | 171439.7998 | 867.199 | 0.2526% | 0.25% | 0.5026% | 0.05026% | 1744.398 | 0.5075% | 2.507% | 0.2507%
|  |  |  | 22.5 | 42859.95 | 224.2997 | 0.2613% | 0.25% | 0.5113% | 0.02557% | 458.5995 | 0.5336% | 2.534% | 0.1267%
|  |  |  | IO | Outputs 4..20mA and 0..10VDC (4 pin M12 Plug) | IO
|  |  |  | CAN | Can-Bus Version (VS, GND, CANHI, CANLO) (4 pin M12 Plug) | CAN
|  |  |  | MOD | MOD-Bus Version (VS, GND, A, B) (4 pin M12 Plug) | MOD
|  |  |  | IO-MOD | Outputs 4..20mA, 0..10VDC, Pulses, MOD-Bus (8 pin M12 Plug) | IO-MOD
|  |  |  | IO-CAN | Outputs 4..20mA, 0..10VDC, Pulses, CAN-Bus (8 pin M12 Plug) | IO-CAN
|  |  |  | D0 | no Display (settings by systec) o.R. | D0
|  |  |  | D1 | integrated display / keypad | D1
|  |  |  | DS | Standard 3% o.S. 1:5 | DS
|  |  |  | DH | High Precision 1% o.S. 1:10 incl 5 point calibration | DH
[5 empty] | none | -
|  |  |  | RSXX | Hot Tap Accessorie for pipe dimesnions 45..335mm | RSXX
|  |  |  | M12-4 | M12 cable 1,5m 4pin | M12-4
|  |  |  | M12-8 | M12 cable 1,5m 8pin | M12-8
|  |  |  | PinBelegung |  | IO | CAN | MOD | IO-MOD | IO-CAN
|  |  |  | (brown) GND | 1 | (brown) GND | (brown) GND | (brown) GND | (white) GND | (white) GND
|  |  |  | (white) 4..20mA | 2 | (white) 4..20mA | (white) CAN hi | (white) Modbus A | (brown) 4..20mA | (brown) 4..20mA
|  |  |  | (blue) Supply | 3 | (blue) Supply | (blue) Supply | (blue) Supply | (green) Supply | (green) Supply
|  |  |  | (black) 0..10VDC | 4 | (black) 0..10VDC | (black) CAN low | Modbus B | (yellow) 0..10VDC | (yellow) 0..10VDC
|  |  |  | n.a. | 5 | n.a. | n.a. | n.a. | (grey) Pulse + | (grey) Pulse +
|  |  |  | n.a. | 6 | n.a. | n.a. | n.a. | (pink) Pulse - | (pink) Pulse -
|  |  |  | n.a. | 7 | n.a. | n.a. | n.a. | (blue) Modbus A | (blue) CAN hi
|  |  |  | n.a. | 8 | n.a. | n.a. | n.a. | (red) Modbus B | (red) CAN low
KEPS) * p/dp * 4096^2/16000
KEPS=(1−𝐸𝑝𝑠𝑖𝑙𝑜𝑛) * p/dp * 4096^2/16000
Epsilon=1-(KEPS*dp/p*16000/4096^2)

## Output Protocol_D
DFC2 Protokoll |  |  |  | 2025-12-12
| Grundtyp | Ausgänge | Display | Genauigkeit | Zubehör | thyssenkrupp Steel Europe AG 22363-02 DFC224260033
DFC2 | P10 | IO | D1 | DH | - | Min recommended diameter is 25mm, please use Venturi
Gastyp | other gas | - |  | 12321 | [kg/Nm³] | 0°C, 1013,25 hPa
Prozess Druck |  |  | 100 | [kPa] |  | Pipe ID | 50 | [mm]
Prozess Temperatur |  |  | 19 | [°C]
Prozess max Durchfluss |  |  | 450 | [Nm3/h]@0°C/1013,25mbar
ImprooveIT |  |  | 1 | [-]
Ergebnisse Auslegung |  | C:\Users\OliverB\Desktop\[deltaflowC2-SelectorV3_08.xlsx]Inputs
[7 empty] | Pin | IO
Max möglicher Durchfluss [MF] |  |  | 26.8158 | [Nm3/h]@0°C/1013,25mbar |  |  | 1 | (brown) GND
Design Durchfluss [DF] |  |  | 450 | [Nm3/h]@0°C/1013,25mbar |  |  | 2 | (white) 4..20mA
Design Druck |  |  | 100 | bar abs |  |  | 3 | (blue) Supply
Design Temperatur |  |  | 19 | °C |  |  | 4 | (black) 0..10VDC
Design Dichte |  |  | 11369.0626 | kg/m³ |  |  | 5 | n.a.
dp am Designpunkt |  |  | 71.052 | [mbar] |  |  | 6 | n.a.
Druckverlust am Auslgungspunkt |  |  | 14.8792 | [mbar] |  |  | 7 | n.a.
Epsilon am Designpunkt |  |  | 0.957 | [-] |  |  | 8 | n.a.
DesignFlow is too high or wrong p&T! Please select other Type or Diameter
Geräteeinstellungen (Option D1)
Flow Unit / Time Basis | [Nm3/h]@0°C/1013,25mbar |  | Damping |  | select [0..99] sek |  | 0-Suppression | select [0..20%] o.S.
Flowspan | 26.8158 | [Nm3/h]@0°C/1013,25mbar | Current Out |  | select [Flow/dp/p/T] |  | KEPS | 2001.4916
Temp. Unit | [°C] |  | Voltage Out |  | select [Flow/dp/p/T] |  | K Analog | 314042.8655
Press. Unit | [kPa] |  | Modbus Brate |  | select [4800..38400]
T. type | Pitot |  | Pulse Length |  | select[2, 10, 100] mS
dp press. Unit | [mbar] |  | Pulse Count |  | select [0..9] p/unit |  |  | FALSE
Unsicherheiten (typisch)
* Nach Installation und im geeigneten Wartungsintervall ist ein Nullpunktabgleich durchzuführen | [7 empty] | V3.07 29.07.2024
© systec Controls Mess- und Regeltechnik GmbH, Lindberghstraße 4, 82178 Puchheim, Germany
www.systec-controls.de - Fon: +49-(0)89-809060 - Fax: +49-(0)89-80906-200 - Email: info@systec-controls.de

## Output Protocol_E
DFC2 Protocoll |  |  |  | 2025-12-12
| Basic Type | I/O_Variant | Display | Accuracy | Accessories | Test
DFC2 | P10 | IO | D1 | DH | - | Min recommended diameter is 25mm, please use Venturi
Gas type | other gas | - |  | 12321 | [kg/Nm³] | 0°C, 1013,25 hPa
Process Pressure |  |  | 100 | [kPa] |  | Pipe ID | 50 | [mm]
Process Temperature |  |  | 19 | [°C]
Process max flow |  |  | 450 | [Nm3/h]@0°C/1013,25mbar
ImprooveIT |  |  | 1 | [-]
Calculated Results |  | C:\Users\OliverB\Desktop\[deltaflowC2-SelectorV3_08.xlsx]Inputs
[7 empty] | Pin | IO
Maximum Flow [MF] |  |  | 26.8158 | [Nm3/h]@0°C/1013,25mbar |  |  | 1 | (brown) GND
Design Flow [DF] |  |  | 450 | [Nm3/h]@0°C/1013,25mbar |  |  | 2 | (white) 4..20mA
Design Pressure |  |  | 100 | bar abs |  |  | 3 | (blue) Supply
Design Temperature |  |  | 19 | °C |  |  | 4 | (black) 0..10VDC
Design Density |  |  | 11369.0626 | kg/m³ |  |  | 5 | n.a.
dp at Operational Flow |  |  | 71.052 | [mbar] |  |  | 6 | n.a.
presser loss at maxflow |  |  | 14.8792 | [mbar] |  |  | 7 | n.a.
Epsilon Expansionnumber |  |  | 0.957 | [-] |  |  | 8 | n.a.
DesignFlow is too high or wrong p&T! Please select other Type or Diameter
Display Settings (Option D1)
Flow Unit / Time Basis | [Nm3/h]@0°C/1013,25mbar |  | Damping |  | select [0..99] sek |  | 0-Suppression | select [0..20%] o.S.
Flowspan | 26.8158 | [Nm3/h]@0°C/1013,25mbar | Current Out |  | select [Flow/dp/p/T] |  | KEPS | 2001.4916
Temp. Unit | [°C] |  | Voltage Out |  | select [Flow/dp/p/T] |  | K Analog | 314042.8655
Press. Unit | [kPa] |  | Modbus Brate |  | select [4800..38400]
T. type | Pitot |  | Pulse Length |  | select[2, 10, 100] mS
dp press. Unit | [mbar] |  | Pulse Count |  | select [0..9] p/unit |  |  | FALSE
Uncertaincy (typical)
* Please proceed zero offset after installation and in an adequate service intaervall | [7 empty] | V3.07 29.07.2024
© systec Controls Mess- und Regeltechnik GmbH, Lindberghstraße 4, 82178 Puchheim, Germany
www.systec-controls.de - Fon: +49-(0)89-809060 - Fax: +49-(0)89-80906-200 - Email: info@systec-controls.de

## Berechnung Unsicherheit (hidden)
Berechnung Unsicherheit
Messbereich max |  | 26.8158 | [Nm3/h]@0°C/1013,25mbar
Messbereich kunde |  | 450 | [Nm3/h]@0°C/1013,25mbar | 450
dp Kunde |  | 71.052 | [mbar]
p Design |  | 1 | [bara]
T Design |  | 292.15 | [K]
dp Nullpunkt |  | 0.1 | [mbar]
Flow [Nm3/h]@0°C/1013,25mbar | dp [mbar] | Uncertaincy o.V. Std | Uncertaincy o.S. Std | Uvertainca o.V. HP | Unsicherhiet dp d.M. | Unsicherheit Dichte | Uncertaincy absolute | Uncertaincy o.S. [DF] | Uncertaincy o.S. [MF]
450 | 71.052 | 3% |  | 1.5% | 0.5688% | 0.9195% | 1.081% | 1.081% | 9.544%
427.5 | 64.1244 | 3.158% |  | 1.579% | 0.5763% | 0.9195% | 1.085% | 1.031% | 9.188%
405 | 57.5521 | 3.333% |  | 1.667% | 0.5852% | 0.9195% | 1.09% | 0.9809% | 8.838%
382.5 | 51.3351 | 3.529% |  | 1.765% | 0.5956% | 0.9195% | 1.096% | 0.9312% | 8.496%
360 | 45.4733 | 3.75% |  | 1.875% | 0.6081% | 0.9195% | 1.102% | 0.8819% | 8.164%
337.5 | 39.9668 | 4% |  | 2% | 0.6232% | 0.9195% | 1.111% | 0.8331% | 7.843%
315 | 34.8155 | 4.286% |  | 2.143% | 0.6416% | 0.9195% | 1.121% | 0.7848% | 7.536%
292.5 | 30.0195 | 4.615% |  | 2.308% | 0.6644% | 0.9195% | 1.134% | 0.7373% | 7.247%
270 | 25.5787 | 5% |  | 2.5% | 0.6931% | 0.9195% | 1.151% | 0.6909% | 6.978%
247.5 | 21.4932 | 5.455% |  | 2.727% | 0.73% | 0.9195% | 1.174% | 0.6457% | 6.737%
225 | 17.763 | 6% |  | 3% | 0.7785% | 0.9195% | 1.205% | 0.6024% | 6.532%
202.5 | 14.388 | 6.667% |  | 3.333% | 0.8439% | 0.9195% | 1.248% | 0.5616% | 6.373%
180 | 11.3683 | 7.5% |  | 3.75% | 0.9354% | 0.9195% | 1.312% | 0.5247% | 6.279%
157.5 | 8.7039 | 8.571% |  | 4.286% | 1.069% | 0.9195% | 1.41% | 0.4934% | 6.277%
135 | 6.3947 | 10% |  | 5% | 1.274% | 0.9195% | 1.571% | 0.4713% | 6.413%
112.5 | 4.4408 | 12% |  | 6% | 1.613% | 0.9195% | 1.857% | 0.4642% | 6.767%
90 | 2.8421 | 15% |  | 7.5% | 2.234% | 0.9195% | 2.416% | 0.4832% | 7.499%
67.5 | 1.5987 | 20% |  | 10% | 3.564% | 0.9195% | 3.681% | 0.5521% | 8.971%
45 | 0.71052 | 30% |  | 15% | 7.273% | 0.9195% | 7.331% | 0.7331% | 12.2%
22.5 | 0.17763 | 60% |  | 30% | 25.42% | 0.9195% | 25.43% | 1.272% | 21.33%

## P10 Druckverlust (hidden)
ID[mm] | Blockage | ploss[%]DF12 | Ploss DFC
25 | 0.73339 | 32 | 48%
30 | 0.5093 | 21.1 | 31.65%
35 | 0.45213 | 18.4 | 27.6%
40 | 0.40585 | 16.3 | 24.45%
50 | 0.33614 | 13.4 | 20.1%
60 | 0.28648 | 11.4 | 17.1%
70 | 0.24945 | 10 | 15%
80 | 0.22083 | 8.9 | 13.35%
100 | 0.17953 | 7.4 | 11.1%
150 | 0.12223 | 4.9333 | 7.4%
200 | 0.092628 | 2.4667 | 3.7%
500 | 0.037739 | 0.49333 | 0.74%
5000 | 0.0038151 | 0.0098667 | 0.0148%