## Gases
This Excel-Sheet is to calculate the SYS-MMF Settings for Gas-Flow only!
Depending if you are using a ISO5167 primary Element or a pitot tube, please use the left or the right Box
Enter your design data in the blue marked fields, the specific seetings for the SYS-MMF can be found on the bottom of the box
Orifice/Venturi/Nozzle |  |  | Pitot tube
C | 0.665 | [-] | K | 0.56817 | [-]
D(warm) | 205.3 | [mm] | D(warm) | 107.3 | [mm] | Calculations |  |  | Calculations
d(warm) | 107.55 | [mm] |  |  |  | A | 0.0090847 | [m²] | A | 0.0090425 | [m²]
RhoN | 0.745 | [kg/Nm³] | RhoN | 1.2929 | [kg/Nm³] | beta | 0.52387 | [-]
[6 empty] | K | 0.69155 | [-]
Prozess Data |  |  | Prozess Data |  |  | q0 | 11.3103 |  | q0 | 29.709
Design p | 225 | [kPa] | Design p | 100 | [kPa] | q1 | 11.3103 |  | q1 | 29.709
Design T | 55 | [°C] | Design T | 20 | [°C] | Last Bit | 0 |  | Last Bit | 0
Design Flow | 12000 | [Nm³/h] | Design Flow | 200 | [Nm³/h] | Buildt | 011,3103000 |  | Buildt | 029,7089700
Design dp | 288.5 | [mbar] | Design dp | 14.99 | [mbar] | Keps | 0.31976 |  | Keps | 0
Design e | 0.959 | [-] | Design e | 1 | [-]
Settings for SYS MMF |  |  | Settings for SYS MMF
Medium | Gas |  | Medium | Gas
Flow Rate | 12000 | [Nm³/h] | Flow Rate | 200 | [Nm³/h]
Flow Coeff | 011,3103000 |  | Flow Coeff | 029,7089700
KEPS | 000,3197574 |  | KEPS | 000,0000000

## Steam or Water
This Excel-Sheet is to calculate the SYS-MMF Settings for Steam or Water -Flow only!
Depending if you are using a ISO5167 primary Element or a pitot tube, please use the left or the right Box
Enter your design data in the blue marked fields, the specific seetings for the SYS-MMF can be found on the bottom of the box
Orifice/Venturi/Nozzle |  |  | Pitot tube
C | 0.60182 | [-] | K | 0.62339 | [-]
D(warm) | 500.18 |  | D(warm) | 500.18 | [mm] | Calculations |  |  | Calculations
d(warm) | 250.09 | [mm] |  |  |  | A | 0.049123 | [m²] | A | 0.19649 | [m²]
Fluid |  |  | Fluid |  |  | beta | 0.5 | [-]
[6 empty] | K | 0.62156 | [-]
Prozess Data |  |  | Prozess Data |  |  | Massenfluss | 380 | [kg/h] | Massenfluss | 380 | [kg/h]
Design p | 2700 | [kPa] | Design p | 2700 | [kPa] | q0 | 155.4465 |  | q0 | 622.3725
Design T | 50 | [°C] | Design T | 50 | [°C] | q1 | 155.4465 |  | q1 | 622.3725
Design Desnity | 989.1747 | [kg/m³] | Design Desnity | 989.1747 | [kg/m³] | Last Bit kg | 0 |  | Last Bit kg | 0
Design Flow | 380 | [kg/h] | Design Flow | 380 | [kg/h] | Last Bit usereinheit | 0 |  | Last Bit usereinheit | 0
Design dp | 59.115 | [mbar] | Design dp | 3.673 | [mbar] | Buildt | 155,4465200 |  | Buildt | 622,3725000
Design e | 1 | [-] | Design e | 0.998 | [-] | Keps | 0 |  | Keps | 14.7019
Settings for SYS MMF |  |  | Settings for SYS MMF
Medium | Suph_Steam |  | Medium | Suph_Steam |  | Superheated Steam |  | 1
Flow Rate | 380 | [kg/h] | Flow Rate | 380 | [kg/h] | Saturated Steam
Flow Coeff | 155,4465200 |  | Flow Coeff | 622,3725000 |  | Water
KEPS | 000,0000000 |  | KEPS | 014,7018786

## other Liquids
This Excel-Sheet is to calculate the SYS-MMF Settings for Liquids-Flow only!
Depending if you are using a ISO5167 primary Element or a pitot tube, please use the left or the right Box
Enter your design data in the blue marked fields, the specific seetings for the SYS-MMF can be found on the bottom of the box
Orifice/Venturi/Nozzle |  |  | Pitot tube
C | 0.60182 | [-] | K | 0.66809 | [-]
D(warm) | 500.18 |  | D(warm) | 500.18 | [mm] | Calculations |  |  | Calculations
d(warm) | 250.09 | [mm] |  |  |  | A | 0.049123 | [m²] | A | 0.19649 | [m²]
[6 empty] | beta | 0.5 | [-]
[6 empty] | K | 0.62156 | [-]
Prozess Data |  |  | Prozess Data |  |  | Massenfluss | 375886.386 | [kg/h] | Massenfluss | 375886.386 | [kg/h]
Design p | 2700 | [kPa] | Design p | 2700 | [kPa] | q0 | 155.4465 |  | q0 | 668.3362
Design T | 50 | [°C] | Design T | 50 | [°C] | q1 | 155.4465 |  | q1 | 668.3362
Design Desnity | 989.1747 | [kg/m³] | Design Desnity | 989.1747 | [kg/m³] | Last Bit kg | 0 |  | Last Bit kg | 0
Design Flow | 380 | [kg/h] | Design Flow | 380 | [kg/h] | Last Bit usereinheit | 0 |  | Last Bit usereinheit | 0
Design dp | 59.115 | [mbar] | Design dp | 3.673 | [mbar] | Buildt | 155,4465200 |  | Buildt | 668,3362200
[6 empty] | Keps | 0 |  | Keps | 0
Settings for SYS MMF |  |  | Settings for SYS MMF
Medium | Liquid |  | Medium | Liquid
Density | 989.1747 | [kg/m³] | Denstity | 989.1747 | [kg/m³]
Flow Rate | 380 | [kg/h] | Flow Rate | 380 | [kg/h]
Flow Coeff | 155,4465200 | [-] | Flow Coeff | 668,3362200 | [-]